## Corrected load calculations
Name: | [7 empty] | HINT: USE TAB KEY OR SHIFT+TAB TO MOVE BETWEEN CELLS
Address:
STEP 1 | Estimate General Electric Load Excluding Heating and AC
[10 empty] | Watts (Volt Amps) | Final Watts (Volt Amps)
Square Footage of Structure |  |  |  | General Lighting Load |  | 3 | Watts per square foot |  | = | 0 | 0
# of Small Appliance Circuits (2 min.) |  |  |  | Small Appliance Circuits |  | 1500 | Watts each |  | = | 0 | 0
# of Laundry Circuits (1 min.) |  |  |  | Laundry Circuits |  | 1500 | Watts each |  | = | 0 | 0
New Construction? | [5 empty] | Step 1 Total = |  |  |  | 0 | 0 |  | Yes
No
STEP 2 | Estimate Heating/AC Electric Load
A/C Condenser & Fixed Space Heating |  | Circuit Shared / Paused With: (please select all shared) | # of units |  | Watts (Volt Amps) |  |  |  |  | Preliminary Watts (Volt Amps) | Final Watts (Volt Amps) | Common Values
A/C Heat up to 8 kW |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 8000 | A/C Heat up to 8 kW
A/C Heat up to 15 kW |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 14000 | A/C Heat up to 15 kW
A/C Heat up to 20 kW |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 20000 | A/C Heat up to 20 kW
Cond/Heat Pump to 2 T |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 2000 | Clothes Dryer
Cond/Heat Pump to 4 T |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 4000 | Cond/Heat Pump to 2 T
Cond/Heat Pump to 5 T |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 7000 | Cond/Heat Pump to 4 T
Cond/Heat Pump to 5 T
Other Electric Heating Device |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 1500 | Cook Range
Cook Oven
[6 empty] | Step 2 Total = |  |  |  | 0 | 0 |  | Dishwasher
Disposal
STEP 3 | Estimate Other Electric Load | [11 empty] | Electric Water Heater
Dedicated Equipment |  | Circuit Shared / Paused With: (please select all shared) | # of units |  | Watts (Volt Amps) |  |  |  |  | Preliminary Watts (Volt Amps) | Final Watts (Volt Amps) | Common Values | EVSE
Electric Water Heater |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 4500 | Heat Pump Water Heater
Refrigerator |  | Not Available to Share |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 1400 | Instant Hot Water Unit
Freezer |  | Not Available to Share |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 600 | Jacuzzi Tub
Dishwasher |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 1200 | Microwave
Disposal |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 800 | Mini Fridge
Range Hood |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 600 | Other Electric Heating Device
Microwave |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 1500 | Patio Heaters
Mini Fridge |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 900 | Pool Heater
Instant Hot Water Unit |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | N/A | Pool Light
Jacuzzi Tub |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 800 | Pool Motor
EVSE |  |  |  | x |  | Volt Amps from Label |  | x 1.25 | = | 0 | 0 | N/A | Range Hood
Res. Elevator |  | Not Available to Share |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | N/A
[6 empty] | Step 3 Total = |  |  |  | 0 | 0
STEP 4 | Estimate Major Equipment Load
Major Equipment |  | Circuit Shared / Paused With: (please select all shared) | # of units |  | Watts (Volt Amps) |  |  |  |  | Preliminary Watts (Volt Amps) | Final Watts (Volt Amps) | Common Values
Cook Range |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 8000
Cook Oven |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 5000
Clothes Dryer |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 5000
Pool Motor |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | N/A
Pool Heater |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | N/A
Pool Light |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 300
Patio Heaters |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | 1500
[6 empty] | Step 4 Total = |  |  |  | 0 | 0
Heat Pump Water Heater |  |  |  | x |  | Volt Amps from Label |  |  | = | 0 | 0 | N/A
STEP 5 | Determine If Electric Service Panel Requires Upgrade
Total General Load excl Heating/AC (Add Steps 1, 3 and 4 Totals) |  |  |  |  | 0 | (Box 1)
Heat Pump Water Heater Electrical Load |  |  |  |  | 0 | (Box 2)
General Service Load (Add Box 1 + Box 2) |  |  |  |  | 0 | (Box 3)
First 10,000 Volt Amps counted at 100% |  |  | 10000 |  | 0 | (Box 4)
Remaining General Service Load at 40% (Box 3 - 10000) x 40% |  |  |  |  | 0 | (Box 5)
Heating/Cooling Load at 100% (from Step 2 Total) |  |  |  |  | 0 | (Box 6)
TOTAL ADJUSTED HOUSE LOAD (Add Box 4 + Box 5 + Box 6) |  |  |  |  | 0 | (Box 7)
Minimum Service Ampacity (Box 7 divided by 240) |  |  |  |  | 0 | (Box "A")
Enter Your Existing or Proposed Electrical Service Size (amps) | [5 empty] | (Box "B")
You need to upgrade your service panel
Service panel upgrade is required!
NOTE: | For One-Family Dwellings, the service disconnecting means shall have a rating of not less than 100 amps, 3-wire.

## Sheet1 (hidden)
Device | Voltamps
A/C Heat up to 8 kW | 0
A/C Heat up to 15 kW | 0
A/C Heat up to 20 kW | 0
Cond/Heat Pump to 2 T | 0
Cond/Heat Pump to 4 T | 0
Cond/Heat Pump to 5 T | 0
Other Electric Heating Device | 0
Electric Water Heater | 0
Refrigerator | 0
Freezer | 0
Dishwasher | 0
Disposal | 0
Range Hood | 0
Microwave | 0
Mini Fridge | 0
Instant Hot Water Unit | 0
Jacuzzi Tub | 0
EVSE | 0
Res. Elevator | 0
Cook Range | 0
Cook Oven | 0
Clothes Dryer | 0
Pool Motor | 0
Pool Heater | 0
Pool Light | 0
Patio Heaters | 0
Heat Pump Water Heater | 0